## Raised floor Finish
SPECIFICATION OF RAISED ACCESS FLOOR SYSTEM - ESRG SYSTEM
Sr No | Particular | Application | Unit | Total Quantity | Rate | Amount
1 | Providing and fixing raised floor system as per below mentioned specification
PANELS : Access Floor panel of size 600 x 600 mm shall be all steel welded construction with an enclosed bottom pan of hemispherical cones and the top plain sheet is fuse-welded at 144 locations to form a panel. The hollow panels post manufacturing shall be pretreated on an Automated Pre treatment line and further coated with electrostatically deposited epoxy raisin paint 60 - 80 micron thick on all the exposed sides of the panel. Post-coating the hollow core of the panel is injected with a lightweight, fire retardant, non-combustible cementitious compound at high pressure to ensure support of not less than 90% of the top surface area of the panel. The panel is then laminated with floor grade Antistatic Laminate / PVC on a semi-automated lamination line to ensure maximum bonding to the steel surface. The edges of the laminated are protected with conductive PVC edge trim 5mm wide on all sides. This edge trim is mechanically locked and sealed in place to avoid detachment.
PANEL DESIGN REQUIREMENT :  The Panel should have a Low Flange Width of 8.00mm on all four sides: - Providing a higher strength to the unsupported edge thus leading to reduced risks and minimalistic damage due to frequent access to the panel post installation - Enabling the panel to perform better on all technical parameters & with enhanced load-bearing capacity - Reducing risk of accidents at site, due to less exposed area while stacking the material at site  Beam width of the panel should be 19.50mm: - Enhances load-bearing capacity by ensuring full support on the entire perimeter, through the beam of the panel when used with the ESRG system  The panel resting on the pedestal head should have a minimum footprint area of not less than 730 sq mm: - Higher footprint area of the panel on the pedestal head enhances the load-bearing capacity of the panel, proving an increased support to the panel  Corner Radius of the panel should be R 15mm & with reduced cantilever flange edge of 19.60mm: - Panel with lower radius, improves reducing the exposed cantilever edge on the unsupported areas at the corners of the panel.  LEED/Green Certified product. - All panels to have a recycle content of minimum 30%. - The panels should be Green certified by a Green building council authority.
SUB STRUCTURE -PEDESTAL ASSEMBLY : Substructure installed to support the panel shall be suitable to achieve a minimum finished floor height of 150 mm to a maximum of 2000 mm from the existing floor level. Pedestal design shall confirm speedy assembly and removal for relocation and maintenance. The assembly shall provide easy adjustment of levelling and accurately align panels for a maximum ± 25 mm in the vertical direction. Pedestals shall support an axial load without permanent deflection and an ultimate load as laid out in System Performance requirement. The Pedestal head assembly shall consist of embossed head mechanically riveted to a rolled formed stud and 2 check nuts for level adjustment and arresting vertical movement. The pedestal head shall consist of an anti-vibrational conductive cap with inbuilt isolating spacers for Panel and stringer location. The Pedestal Base assembly shall consist of pipe mechanically locked on a press for perpendicularity and then mechanically welded to a base plate with stiffening folds for enhanced strength & excellent grip to glue. The substructure assembly shall be suitably anchored to the floor with suitable adhesive or fastener as recommended by the consultant/manufacturer. All steel components shall be pre Galvanized.
STRINGERS : The stringer shall be Continuous Box type, hot dipped galvanized steel cold rolled construction for strength, lateral stability, and for enhanced rolling loads performance and to support the panels on all four sides for alignment without leaving any gap at the pedestal head preventing air leakage. The stringer to have countersunk holes at both ends to accommodate bolting of M6 machine screws to the pedestal head assembly.
PERFORMANCE CONFORMING TO MASTER SPECS 10270 / 096900 ( USA )
A: Structural Performance: CISCA A/F, ‘Recommended Test Procedures for Access Floors’
Concentrated Loads : 363 Kgs (800 lbf ) with a top-surface deflection under load and a permanent set not to exceed 2.54 & 0.25 mm (0.10 & 0.010 inches) respectively according to CISCA A/F, Section I ‘’ Concentrated Loads’’
Ultimate Concentrated Load: 907 kgs (2000 lbf) without failing according to CISCA A/F, Section II ‘’ Ultimate Loading’’
Uniformly Distributed Load (UDL) : 1650 kg/m2 1650 kg/m2 with a maximum permissible deflection of not more than 2.5 mm as per definition of “Uniform load” of CISCA.
Pedestal Axial Load Test : 22 kN axial Load per pedestal, according to CISCA A/F, Section V, ‘’Pedestal Axial Load Test ’’
Pedestal Over Turning Moment Test : 113 N x meters, according to CISCA A/F, Section VI, ‘’Pedestal Overturning Moment Test’’
Rolling Loads : 180 kgs ( 400 lbf) of the following magnitude, with a combination of local and overall deformation not to exceed 1.02 mm (0.040 inches) according to CISCA A/F, Section III ‘’ Rolling Loads’’ CISCA AF Rolling Load: 10000 Passes
B: Other Optional Structural Parameters :
Soft body impact test on the system shall be with a load of 40 kgs dropped form a height of 1000 mm and shallcomply to all the performance as specified in the test method (T12.03) of MOB PF2 PS Standards.
Hard body impact test on the system shall be with 4.5 kgs dropped from a height of 600 mm and shall comply to all the performance as specified in the test method (T13.03) of MOB PF2 PS Standards.
C: Other Nonstructural Parameters:
Fire Rating : The Panels shall confirm to Class O & Class 1 Fire Ratings tested as per BS 476 Part 6 (Fire Propagation) & 7 (Surface spread of flame) and also BS 476 Part 4:1970 (Non -Combustibility)
Electrical Resistivity: As per ASTM F150/ NFPA 99 / ANSI S7.1 / CEI 61340 but modified for the surface to ground. To place one electrode on the Access floor Panel surface and to attach the other electrode on the pedestal. Resistance to be tested at 100/500 volts 1. Conductive range : 2.5x104 – 1x 106 Ohms (surface to ground) 2. Static dissipative range : 1x106 – 1x109 Ohms (surface to ground) 3. Anti static range : 1x109 – 2x1010 Ohms (surface to surface)
Fabrication Tolerance : A. Floor panel flatness: ± 0.75 mm in any direction B. Floor panel width or length from specified size: ± 0.50mm C. Floor panel squareness: ± 0.38 mm
Installation Tolerance : A. Overall level before application of any load : ± 1.5 mm over any 5.00 Sqmt (or) ± 6 mm over any size of basic space. B. Panel level : + 0.75 mm before the application of any load C. Panel Interchangeability installation and removal shall be interchangeable (except for field cut panels) and replaceable in any of the four directions at 90º increments
Sub structure - pedestal assembly installed to support the panel shall be suitable to achieve a minimum finished floor height as follows
a) | FFH 65 - 300 mm High (Low Lock) |  | Sqm | 0 |  | 0
FFH 300 - 600 mm High (Regular)
FFH 600 - 900 mm High (Heavy Duty)
FFH 900 - 1500 mm High (Extra Heavy Duty)
2 | Raised Floor Ramps : Specification & loading factors of Bare panels to be considered as per respective items |  | Sqm | 0 |  | 0
Ramp Sub Structure Pedestal Assembly : Sub structure installed to support the panel shall be suitable to achieve slop of 1:12 ratio or as specified in the approved drawing, from the existing floor level to the finished cavity floor level. Pedestal design shall confirm speedy assembly and removal for relocation and maintenance. The assembly shall provide easy adjustment of leveling and accurately align panels for a maximum 25 mm in perpendicular direction to the pedestal assembly. Each pedestal to have an appropriate swivel head to adjust to the slope degree with appropriate locking mechanism, pedestals shall support an axial load without permanent deflection and an ultimate load and other requirement as laid out in system performance requirement.
The sub structure assembly shall be suitably anchored to the floor with suitable adhesive / bolts as recommended by the consultant / manufacturer. All steel components shall be pre Galvanized.
3 | Heavy Duty Ramp Shoe / Threshold : Providing and fixing Ramp Shoe of heavy-duty anodized aluminum. The Shoe ramp must have a trapezoid anchoring leg, which is firmly secured to the concrete floor. The system should be securely fastened to the concrete floor at regular intervals with the use of fasteners. The profile should protect tile edges to eliminate trip hazards and ensures easy access of trolleys. The ramp shoe a full 15 inches wide & protects the ramp from equipment damage and makes an excellent seamless transition between two surfaces. |  | No | 0 |  | 0
| Total Amount |  |  |  |  | 0

## Bare Raised Flooring (hidden)
SPECIFICATION OF - BARE RAISED FLOOR SYSTEM
Sr No | Particular | Location | Unit | Quantity | [7 empty] | Total Quantity | Rate | Amount
|  |  |  | 8th | 9th | 10th | 11th | 12th |  | 14th
[8 empty] | Citi | CGM | Citi | CGM
1 | Bare Raised Flooring
Providing and fixing raised floor system as per below mentioned specification
Bare Panels
Nominal size of floor panel : 600 mm x 600 mm
Permissible thickness : 35 mm
Concentrated Loads : 450 Kgs ( 1000 lbf ) with a top-surface deflection under load and a permanent set not to exceed , respectively, 2.54 & 0.25 mm ( 0.10 & 0.010 inch ) according to CISCA A/F, Section I ‘’ Concentrated Loads’’
Ultimate Concentrated Load: 1125 kgs (2500 lbf ) without failing according to CISCA A/F, Section II ‘’ Ultimate Loading’’
Rolling Loads : 225 kgs ( 500 lbf )of the following magnitude, with a combination of local and overall deformation not to exceed1.02 mm (0.040 inch) according to CISCA A/F, Section III ‘’ Rolling Loads’’ CISCA AF Rolling Load: 10000 Passes
Pedestal Axial Load Test : 22 kN axial Load per pedestal, according to CISCA A/F, Section V, ‘’Pedestal Axial Load Test ’’
Pedestal Over Turning Moment Test : 113 N x meters, according to CISCA A/F, Section VI, ‘’Pedestal Overturning Moment Test’’
Uniformly Distributed Load (UDL) : 1350 kg/m2 with a maximum permissible deflection of not more than 1.52 mm as per definition of “Uniform load” of CISCA tested over an area of 300x300 mm square for 126 kgs load
Fire Rating : The Panels shall confirm to Class O & Class 1 Fire Ratings tested as per BS 476 Part 6 (Fire Propagation) & 7 (Surface spread of flame) as also ASTM E84 1998 (Flammability) and ASTM E136 (Combustibility)
Panels : Access Floor panel of size 600x600 mm shall be all steel welded construction, with an enclosed bottom pan and top plain sheet which are fuse welded at various locations to form a panel of an overall thickness of 35mm. The panel after cleaning, degreasing, to the panel surface and corrosion resistance. The inner empty core of the panel shall be injected with a light weight fire retardant, non combustible cementitious compound at high pressure to fill in all the crevices of the panel and ensures support of not less than 90% of the top surface area of the panel. The panel shall have located corner holes on all edges for bolting the panel to the substructure to form a rigid monolithic smooth leveled floor.
SUB STRUCTURE -PEDESTAL ASSEMBLY : Sub structure installed to support the panel shall be suitable to achieve a minimum finished floor height of 150 mm to a maximum of 600 mm from the existing floor level. Pedestal design shall confirm speedy assembly and removal for relocation and maintenance. The assembly shall provide easy adjustment of leveling and accurately align panels for a maximum ± 25 mm in the vertical direction. Pedestals shall support an axial load without permanent deflection and an ultimate load as laid out in System Performance requirement. The Pedestal head assembly shall consist of a 75 x 75 x 3.50 mm embossed head mechanically riveted to a 100mm long ¾” dia rolled formed stud and 2 check nuts for level adjustment and arresting vertical movement. The Pedestal Base assembly shall consist of 22.20 mm OD pipe mechanically locked on a press for perpendicularity and then welded to a base plate of 100 x 100 x 2 mm thick with stiffening folds. The sub structure assembly shall be suitably anchored to the floor with suitable adhesive as recommended by the consultant / manufacturer. All steel components shall be zinc electro plated.
There shall be grommets given to corner of tiles to suit the grid design for power / data / voice outlets.
The raised Access Flooring shall be as per PSA MOB PF2/S/SPU standards.
i | 150 mm High | Office Area | Smt | 2568 | 2569 | 1436 | 2588 | 331 | 831 | 1335 | 1224 | 12882 |  | 0
ii | 200 mm High | Trading area | Smt | 0 | 0 | 0 | 0 | 764 | 330 | 0 |  | 1094 |  | 0
2 | Supplying two-cup vacuum suction lifting handles suited to the Raised floor system. |  | Nos
3 | Provide and install 75 mm dia. Heavy Guage PVC grommets with rotating cover and passage for cables in pre-cut openings. The edges of the openings to be properly polished to prevent any injuries |  | Nos
| Total Amount For Bare Raised Flooring | [12 empty] | 0
a | Quantities mentioned above are tentative and will be revised on plan finalisation.contractors are instructed to verify site condititions/measurement before starting procurement of the material.
b | All areas & measurement should be physically checked at site and will be paid accordingly.No separate payment will be given for wastage.

## Measurement (hidden)
Measurement For Raised Flooring - 8th to 12th & 14th Floor
Flase Flooring - 8 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 2517.67 | 2518 | 2568
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.7 | 9 | 9
ii | 450 mm High
| Ter Room | Sqm | 1 | 15.78 | 16 | 16
Flase Flooring - 9 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 2519.31 | 2519 | 2569
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.7 | 9 | 9
ii | 450 mm High
| Ter Room | Sqm | 1 | 23.63 | 24 | 24
Flase Flooring - 10 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room, Housekeeping, BMS | Sqm | 1 | 977.82 | 978
| Mrket Place / Training Room / Passage | Sqm | 1 | 388.24 | 388
| Compactors Room | Sqm | 1 | 14.15 | 14
| Store Room | Sqm | 1 | 28.19 | 28
[5 empty] | 1408 | 1436
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 9.38 | 9 | 9
ii | 450 mm High
| Ter Room | Sqm | 1 | 21.12 | 21 | 21
Flase Flooring - 11 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 2545.5 | 2546
| Less - Shft | Sqm | -2 | 4.27 | -9
[5 empty] | 2537 | 2588
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.044 | 8 | 8
ii | 450 mm High
| Ter Room | Sqm | 1 | 24.49 | 24
| Deluge Room | Sqm | 1 | 8.29 | 8
[5 empty] | 32 | 33
iii | 300 mm High
| UPS Room | Sqm | 1 | 38.55 | 39 | 40
Flase Flooring - 12 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
Citi
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 314.69 | 315
[5 empty] | 315 | 321
ii | 200 mm High
| Trading Area | Sqm | 1 | 727.9 | 728 | 743
2 | Laminated False Flooring
i | 300 mm High
| UPS / UPS Battery Room / Ter Room | Sqm | 1 | 85.15 | 85
[5 empty] | 85 | 87
ii | 150 mm High
| Electrical Room | Sqm | 1 | 9.19 | 9
[5 empty] | 9 | 9
iii | 600 mm High
| Ter Room | Sqm | 1 | 55.96 | 56
| PAC Room | Sqm | 1 | 15.95 | 16
[5 empty] | 72 | 73
CGM
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 677.51 | 658.4
| Print Shop | Sqm | 1 | 47.32 | 47
| Compactor Room | Sqm | 1 | 26.24 | 26
| Passage | Sqm | 1 | 63.07 | 63
|  | Sqm | 1 | 5.61 | 6
| Less - Shft | Sqm | -2 | 4.27 | -9
[5 empty] | 791.4 | 807
ii | 200 mm High
| Trading Area | Sqm | 1 | 314.07 | 314 | 320
2 | Laminated False Flooring
i | 300 mm High
| UPS / UPS Battery Room for CGM | Sqm | 1 | 78.43 | 78
[5 empty] | 78 | 80
ii | 150 mm High
| Electrical Room | Sqm | 1 | 10.65 | 11
[5 empty] | 11 | 11
iii | 600 mm High
| MER For CGM | Sqm | 1 | 140.29 | 140
| PAC Room | Sqm | 1 | 13.54 | 14
| Deluge Room | Sqm | 1 | 6.67 | 7
[5 empty] | 161 | 164
Flase Flooring - 14 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
Citi
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room, Housekeeping, BMS | Sqm | 1 | 1270.67 | 1271
[5 empty] | 1271 | 1296
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.18 | 8
[5 empty] | 8 | 8
CGM
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room, Housekeeping, BMS | Sqm | 1 | 1129 | 1129
| Compactors Room | Sqm | 1 | 23.036 | 23
| Compactors Room | Sqm | 1 | 23.036 | 23
| Less - Shft | Sqm | -2 | 4.27 | -9
[5 empty] | 1166 | 1189
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.83 | 9
[5 empty] | 9 | 9
ii | 450 mm High
| Ter CGM | Sqm | 1 | 24.955 | 25 | 26

## Sheet1 (hidden)
Panel | Top Plate Thickness | 0.50 mm
| Bottom Plate Thickness | 0.60 mm
FFH 100 TO FFH 200 | Base Plate | 85 x 85 x 2.00 mm
| Pipe Outer Dia | 15.23 mm
| Thickness of the Pipe | 1.50 mm
| Head Plate thickness | 75 x 75 x 3.00 mm
| Stud | 1/2'' BSW stud
| Check Nut | 1/2'' BSW threaded