## Raised floor -Bare Finish
SPECIFICATION - BARE RAISED ACCESS FLOOR SYSTEM
Sr No | Particular | Location | Unit | Rate | Total Quantity | Amount
1 | Providing and fixing raised floor system as per below mentioned specification
Panels : Access Floor panel of size 600 x 600 mm shall be all steel welded construction with an enclosed bottom pan of 60 hemispherical cones and top plain sheet fuse welded at 124 locations and folded on all the four perimeters to achieve the greater strength of the edges. The overall thickness of the panel shall be 31 mm. The panel after cleaning, degreasing, phosphating by 11 tank process is coated with 40 – 60-micron epoxy coat and is heated to achieve maximum adhesion to the panel surface and corrosion resistance. The inner empty core of the panel is injected with a lightweight, fire retardant, non-combustible cementitious compound at high pressure to fill in all the crevices of the panel and ensures support of not less than 90% of the top surface area of the panel. The panel shall have 4 locating corner holes with a Self-capturing fastener which will remain within the panel and will not get lost. These fasteners are used for bolting the panel to the substructure to form a rigid monolithic smooth levelled floor.
SUB STRUCTURE -PEDESTAL ASSEMBLY : Substructure installed to support the panel shall be suitable to achieve a minimum finished floor height of 65 -150 mm from the existing floor level. Pedestal design shall confirm speedy assembly and removal for relocation and maintenance. The assembly shall provide easy adjustment of levelling and accurately align panels for a maximum of ± 25 mm in the vertical direction. Pedestals shall support an axial load without permanent deflection and an ultimate load as laid out in System Performance requirement. Note: Higher finished floor heights (FFH) can be made available on request. The Pedestal head design provides self-engagement and positioning of the floor panel. Pedestal assembly shall consist of an embossed head mechanically riveted to a 100mm long ¾” dia rolled formed stud and 2 check nuts for level adjustment and arresting vertical movement. The pedestal head shall consist of an anti-vibration PVC cap with posilock design to provide more structural strength at four corners of the panel for positive panel location. The Pedestal Base assembly shall consist of pipe with mechanically locked on a press for perpendicularity and then welded to a base plate with stiffening folds. The substructure assembly shall be suitably anchored to the floor with a suitable adhesive as recommended by the manufacturer. All steel components shall be Pre- Galvanized.
PERFORMANCE CONFORMING TO MASTER SPECS 10270 / 096900 ( USA )
A: Structural Performance: ‘Recommended Test Procedures for Access Floors’
Concentrated Loads : 454 Kgs (1000 lbf ) with a top-surface deflection under load and a permanent set not to exceed 2.54 & 0.25 mm (0.10 & 0.010 inch) respectively according to CISCA A/F,Section I ‘’ Concentrated Loads’’
Ultimate Concentrated Load: 1134 Kgs (2500 lbf) without failing as per‘’ Ultimate Loading Test’’
Uniformly Distributed Load (UDL) : 2250 kg/m2 The uniform load rating of an access floor panel as specified here in should not be confused with the “uniform live load” as specified in seismic zone application.
Pedestal Axial Load Test : 22 kN axial Load per ‘’Pedestal Axial Load Test ’’
Pedestal Over Turning Moment Test : 113 N x meters, according to CISCA A/F, Section VI, ‘’Pedestal Overturning Moment Test’’
Rolling Loads : 225 kgs ( 500 lbf) of the following magnitude, with a combination of local and overall deformation not to exceed 1.02 mm (0.040 inches) according to CISCA A/F, Section III ‘’ Rolling Loads’’ CISCA AF Rolling Load: 10000 Passes
B: Other Optional Structural Parameters :
Soft body impact test on the system shall be with a load of 40 kgs dropped form a height of 1000 mm and shallcomply to all the performance as specified in the test method (T12.03) of MOB PF2 PS Standards.
Hard body impact test on the system shall be with 4.5 kgs dropped from a height of 600 mm and shall comply to all the performance as specified in the test method (T13.03) of MOB PF2 PS Standards.
C: Other Nonstructural Parameters:
Fire Rating : The Panels shall confirm to Class O & Class 1 Fire Ratings tested as per BS 476 Part 6 (Fire Propagation) & 7 (Surface spread of flame) as also ASTM E84 1998 (Flammability) and ASTM E136 (Combustibility)
Non Combustibility Test:-Fire Test on Building Materials & Structures - Non Cumbustibility Test for Panels in accordance BS 476 Part 4-1970
Sub structure - pedestal assembly installed to support the panel shall be suitable to achieve a minimum finished floor height as follows
a) | FFH 65 - 300 mm High (Low Lock) |  | Sqm | 0 |  | 0
b) | FFH 150 mm - 600 (Regular) |  | Sqm | 0 |  | 0
2 | Raised Floor Ramps : Specification & loading factors of Bare panels to be considered as per respective items |  | Sqm | 0 |  | 0
Ramp Sub Structure Pedestal Assembly : Sub structure installed to support the panel shall be suitable to achieve slop of 1:12 ratio or as specified in the approved drawing, from the existing floor level to the finished cavity floor level. Pedestal design shall confirm speedy assembly and removal for relocation and maintenance. The assembly shall provide easy adjustment of leveling and accurately align panels for a maximum 25 mm in perpendicular direction to the pedestal assembly. Each pedestal to have an appropriate swivel head to adjust to the slope degree with appropriate locking mechanism, pedestals shall support an axial load without permanent deflection and an ultimate load and other requirement as laid out in system performance requirement.
The sub structure assembly shall be suitably anchored to the floor with suitable adhesive / blots as recommended by the consultant / manufacturer. All steel components shall be zinc electro plated.
3 | Heavy Duty Ramp Shoe / Threshold : Providing and fixing Ramp Shoe of heavy-duty anodized aluminum. The Shoe ramp must have a trapezoid anchoring leg, which is firmly secured to the concrete floor. The system should be securely fastened to the concrete floor at regular intervals with the use of fasteners. The profile should protect tile edges to eliminate trip hazards and ensures easy access of trolleys. The ramp shoe a full 15 inches wide & protects the ramp from equipment damage and makes an excellent seamless transition between two surfaces. |  | No | 0 |  | 0
4 | Grommets: Provide and install 75 mm dia. Heavy Guage PVC grommets with rotating cover and passage for cables in pre-cut openings. The edges of the openings to be properly polished to prevent any injuries |  | No | 0 |  | 0
5 | Panel Lifter : Supply of Panel lifter , for lifting heavy loaded tiles. |  | No | 0 |  | 0
6 | Bridges : Providing & Fixing bridge make of MS powder coated with PVC pedestal cap attached & understructure support system to accommodate the raised floor panels. Available in length of 900 mm, 1200 mm and 1500 mm |  | No | 0 |  | 0
| Total Amount |  |  | 0 |  | 0

## Bare Raised Flooring (hidden)
SPECIFICATION OF - BARE RAISED FLOOR SYSTEM
Sr No | Particular | Location | Unit | Quantity | [7 empty] | Total Quantity | Rate | Amount
|  |  |  | 8th | 9th | 10th | 11th | 12th |  | 14th
[8 empty] | Citi | CGM | Citi | CGM
1 | Bare Raised Flooring
Providing and fixing raised floor system as per below mentioned specification
Bare Panels
Nominal size of floor panel : 600 mm x 600 mm
Permissible thickness : 35 mm
Concentrated Loads : 450 Kgs ( 1000 lbf ) with a top-surface deflection under load and a permanent set not to exceed , respectively, 2.54 & 0.25 mm ( 0.10 & 0.010 inch ) according to CISCA A/F, Section I ‘’ Concentrated Loads’’
Ultimate Concentrated Load: 1125 kgs (2500 lbf ) without failing according to CISCA A/F, Section II ‘’ Ultimate Loading’’
Rolling Loads : 225 kgs ( 500 lbf )of the following magnitude, with a combination of local and overall deformation not to exceed1.02 mm (0.040 inch) according to CISCA A/F, Section III ‘’ Rolling Loads’’ CISCA AF Rolling Load: 10000 Passes
Pedestal Axial Load Test : 22 kN axial Load per pedestal, according to CISCA A/F, Section V, ‘’Pedestal Axial Load Test ’’
Pedestal Over Turning Moment Test : 113 N x meters, according to CISCA A/F, Section VI, ‘’Pedestal Overturning Moment Test’’
Uniformly Distributed Load (UDL) : 1350 kg/m2 with a maximum permissible deflection of not more than 1.52 mm as per definition of “Uniform load” of CISCA tested over an area of 300x300 mm square for 126 kgs load
Fire Rating : The Panels shall confirm to Class O & Class 1 Fire Ratings tested as per BS 476 Part 6 (Fire Propagation) & 7 (Surface spread of flame) as also ASTM E84 1998 (Flammability) and ASTM E136 (Combustibility)
Panels : Access Floor panel of size 600x600 mm shall be all steel welded construction, with an enclosed bottom pan and top plain sheet which are fuse welded at various locations to form a panel of an overall thickness of 35mm. The panel after cleaning, degreasing, to the panel surface and corrosion resistance. The inner empty core of the panel shall be injected with a light weight fire retardant, non combustible cementitious compound at high pressure to fill in all the crevices of the panel and ensures support of not less than 90% of the top surface area of the panel. The panel shall have located corner holes on all edges for bolting the panel to the substructure to form a rigid monolithic smooth leveled floor.
SUB STRUCTURE -PEDESTAL ASSEMBLY : Sub structure installed to support the panel shall be suitable to achieve a minimum finished floor height of 150 mm to a maximum of 600 mm from the existing floor level. Pedestal design shall confirm speedy assembly and removal for relocation and maintenance. The assembly shall provide easy adjustment of leveling and accurately align panels for a maximum ± 25 mm in the vertical direction. Pedestals shall support an axial load without permanent deflection and an ultimate load as laid out in System Performance requirement. The Pedestal head assembly shall consist of a 75 x 75 x 3.50 mm embossed head mechanically riveted to a 100mm long ¾” dia rolled formed stud and 2 check nuts for level adjustment and arresting vertical movement. The Pedestal Base assembly shall consist of 22.20 mm OD pipe mechanically locked on a press for perpendicularity and then welded to a base plate of 100 x 100 x 2 mm thick with stiffening folds. The sub structure assembly shall be suitably anchored to the floor with suitable adhesive as recommended by the consultant / manufacturer. All steel components shall be zinc electro plated.
There shall be grommets given to corner of tiles to suit the grid design for power / data / voice outlets.
The raised Access Flooring shall be as per PSA MOB PF2/S/SPU standards.
i | 150 mm High | Office Area | Smt | 2568 | 2569 | 1436 | 2588 | 331 | 831 | 1335 | 1224 | 12882 |  | 0
ii | 200 mm High | Trading area | Smt | 0 | 0 | 0 | 0 | 764 | 330 | 0 |  | 1094 |  | 0
2 | Supplying two-cup vacuum suction lifting handles suited to the Raised floor system. |  | Nos
3 | Provide and install 75 mm dia. Heavy Guage PVC grommets with rotating cover and passage for cables in pre-cut openings. The edges of the openings to be properly polished to prevent any injuries |  | Nos
| Total Amount For Bare Raised Flooring | [12 empty] | 0
a | Quantities mentioned above are tentative and will be revised on plan finalisation.contractors are instructed to verify site condititions/measurement before starting procurement of the material.
b | All areas & measurement should be physically checked at site and will be paid accordingly.No separate payment will be given for wastage.

## Measurement (hidden)
Measurement For Raised Flooring - 8th to 12th & 14th Floor
Flase Flooring - 8 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 2517.67 | 2518 | 2568
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.7 | 9 | 9
ii | 450 mm High
| Ter Room | Sqm | 1 | 15.78 | 16 | 16
Flase Flooring - 9 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 2519.31 | 2519 | 2569
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.7 | 9 | 9
ii | 450 mm High
| Ter Room | Sqm | 1 | 23.63 | 24 | 24
Flase Flooring - 10 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room, Housekeeping, BMS | Sqm | 1 | 977.82 | 978
| Mrket Place / Training Room / Passage | Sqm | 1 | 388.24 | 388
| Compactors Room | Sqm | 1 | 14.15 | 14
| Store Room | Sqm | 1 | 28.19 | 28
[5 empty] | 1408 | 1436
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 9.38 | 9 | 9
ii | 450 mm High
| Ter Room | Sqm | 1 | 21.12 | 21 | 21
Flase Flooring - 11 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 2545.5 | 2546
| Less - Shft | Sqm | -2 | 4.27 | -9
[5 empty] | 2537 | 2588
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.044 | 8 | 8
ii | 450 mm High
| Ter Room | Sqm | 1 | 24.49 | 24
| Deluge Room | Sqm | 1 | 8.29 | 8
[5 empty] | 32 | 33
iii | 300 mm High
| UPS Room | Sqm | 1 | 38.55 | 39 | 40
Flase Flooring - 12 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
Citi
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 314.69 | 315
[5 empty] | 315 | 321
ii | 200 mm High
| Trading Area | Sqm | 1 | 727.9 | 728 | 743
2 | Laminated False Flooring
i | 300 mm High
| UPS / UPS Battery Room / Ter Room | Sqm | 1 | 85.15 | 85
[5 empty] | 85 | 87
ii | 150 mm High
| Electrical Room | Sqm | 1 | 9.19 | 9
[5 empty] | 9 | 9
iii | 600 mm High
| Ter Room | Sqm | 1 | 55.96 | 56
| PAC Room | Sqm | 1 | 15.95 | 16
[5 empty] | 72 | 73
CGM
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room | Sqm | 1 | 677.51 | 658.4
| Print Shop | Sqm | 1 | 47.32 | 47
| Compactor Room | Sqm | 1 | 26.24 | 26
| Passage | Sqm | 1 | 63.07 | 63
|  | Sqm | 1 | 5.61 | 6
| Less - Shft | Sqm | -2 | 4.27 | -9
[5 empty] | 791.4 | 807
ii | 200 mm High
| Trading Area | Sqm | 1 | 314.07 | 314 | 320
2 | Laminated False Flooring
i | 300 mm High
| UPS / UPS Battery Room for CGM | Sqm | 1 | 78.43 | 78
[5 empty] | 78 | 80
ii | 150 mm High
| Electrical Room | Sqm | 1 | 10.65 | 11
[5 empty] | 11 | 11
iii | 600 mm High
| MER For CGM | Sqm | 1 | 140.29 | 140
| PAC Room | Sqm | 1 | 13.54 | 14
| Deluge Room | Sqm | 1 | 6.67 | 7
[5 empty] | 161 | 164
Flase Flooring - 14 th Floor
Sr No | Particulars | Unit | No | Area | Qunatity | 2% Extra
Citi
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room, Housekeeping, BMS | Sqm | 1 | 1270.67 | 1271
[5 empty] | 1271 | 1296
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.18 | 8
[5 empty] | 8 | 8
CGM
1 | Bare Flase Flooring
i | 150 mm High
| Open Office , cabins, Meeting Room, Utility, Quite Room, Housekeeping, BMS | Sqm | 1 | 1129 | 1129
| Compactors Room | Sqm | 1 | 23.036 | 23
| Compactors Room | Sqm | 1 | 23.036 | 23
| Less - Shft | Sqm | -2 | 4.27 | -9
[5 empty] | 1166 | 1189
2 | Laminated False Flooring
i | 150 mm High
| Electrical Room | Sqm | 1 | 8.83 | 9
[5 empty] | 9 | 9
ii | 450 mm High
| Ter CGM | Sqm | 1 | 24.955 | 25 | 26

## Sheet1 (hidden)
Panel | Top Plate Thickness | 0.50 mm
| Bottom Plate Thickness | 0.60 mm
FFH 100 TO FFH 200 | Base Plate | 85 x 85 x 2.00 mm
| Pipe Outer Dia | 15.23 mm
| Thickness of the Pipe | 1.50 mm
| Head Plate thickness | 75 x 75 x 3.00 mm
| Stud | 1/2'' BSW stud
| Check Nut | 1/2'' BSW threaded